## Instructions
Instructions & Data Dictionary
The HTML sizes energy for design year 15. Power is not degradation-derated unless a future manufacturer-specific power-retention field is added.
Field | Required | Unit | Definition | Example
Model_ID | Yes | Text | Unique stable identifier. Duplicate IDs are rejected. | custom-default
Brand | No | Text | Manufacturer or supplier name. | Example Energy
Model_Name | Yes | Text | Customer-facing battery model name. | Custom Model
Gross_Pack_kWh | Yes | kWh | Nameplate energy of one battery pack/container. | 2250
Min_SOC_pct | Yes | % | Minimum permitted SOC. DoD = Max SOC - Min SOC. | 5
Max_SOC_pct | Yes | % | Maximum permitted SOC; must exceed Min SOC. | 100
RTE_pct | Yes | % | Round-trip efficiency. State the measurement boundary in RTE_Definition. | 85
Aux_Retention_pct | Yes | % | Energy retained after auxiliary consumption. 98% means 2% auxiliary loss. | 98
Pack_Rated_Power_kW | Yes | kW | Continuous/rated discharge power per pack used for power-constrained checks. | 1125
PCS_Rated_Power_kW | Yes | kW | Rated power of one PCS unit. | 1125
First_Year_Degradation_pct | Yes | % | Capacity loss applied during year 1. | 2
Annual_Degradation_pct_Years_2_to_15 | Yes | %/year | Annual compounded capacity loss for years 2 through 15. | 1
RTE_Definition | Yes | Text | Examples: AC-to-AC system RTE or battery DC RTE. | AC-to-AC system RTE
Degradation_Notes | No | Text | Manufacturer degradation assumptions or warranty reference.
Source_Notes | No | Text | Datasheet filename, revision, URL or verification note.
Calculated_DoD_pct | Formula | % | Max_SOC_pct - Min_SOC_pct. | 95
Year15_SOH_pct | Formula | % | (1-first-year degradation) x (1-subsequent annual degradation)^14. | 85.14
Year15_Usable_kWh | Formula | kWh | Gross x DoD x RTE x Aux retention x Year-15 SOH. | 1515.95

## Battery_PCS_Library
BESS Battery & PCS Library Import Template
Complete the blue input columns only. Keep Model_ID unique. Calculated green columns are audit outputs; the HTML recalculates them on import.
Model_ID | Brand | Model_Name | Gross_Pack_kWh | Min_SOC_pct | Max_SOC_pct | RTE_pct | Aux_Retention_pct | Pack_Rated_Power_kW | PCS_Rated_Power_kW | First_Year_Degradation_pct | Annual_Degradation_pct_Years_2_to_15 | RTE_Definition | Degradation_Notes | Source_Notes | Calculated_DoD_pct | Year15_SOH_pct | Year15_Usable_kWh
custom-default |  | Custom Model | 1000 | 5 | 100 | 90 | 98 | 500 | 500 | 0 | 1 | AC-to-AC system RTE |  | Default configurable pack
huawei-luna-2000 | Huawei | Luna 2000-215 | 215 | 5 | 100 | 90 | 98 | 100 | 100 | 2 | 1 | AC-to-AC system RTE | Illustrative reference values - verify against the current manufacturer datasheet before use. | Huawei Luna 2000-215 commercial & industrial ESS (approximate nameplate figures).
byd-mc-cube | BYD | MC Cube | 262 | 5 | 100 | 90 | 98 | 130 | 130 | 2 | 1 | AC-to-AC system RTE | Illustrative reference values - verify against the current manufacturer datasheet before use. | BYD MC Cube commercial & industrial ESS (approximate nameplate figures).
catl-enerone | CATL | EnerOne | 372 | 5 | 100 | 90 | 98 | 186 | 186 | 2 | 1 | AC-to-AC system RTE | Illustrative reference values - verify against the current manufacturer datasheet before use. | CATL EnerOne liquid-cooled rack (C&I) - approximate nameplate figures.
tesla-megapack-2xl | Tesla | Megapack 2 XL | 3900 | 5 | 100 | 92 | 99 | 1925 | 1925 | 2 | 0.5 | AC-to-AC system RTE | Illustrative reference values - verify against the current manufacturer datasheet before use. | Tesla Megapack 2 XL (utility/C&I) - approximate nameplate figures.

## Parameter Definitions
BESS Peak-Shaving Sizing Tool — Parameter Definitions
Every input parameter, result field and calculated value across both tabs (Analysis & BESS Sizing · Battery & PCS Library).
Tab | Section | Parameter | Unit | Definition
Analysis & BESS Sizing | Load Data | Upload load profile (.xlsx) or CSV | file | Customer's utility load profile: interval demand readings. The tool parses timestamps and load (kW), plus optional PV-generation and grid-export columns.
Analysis & BESS Sizing | Load Data | Download CSV template | file | Downloads a blank CSV with the expected columns (timestamp, load_kw, pv_gen_kw, grid_export_kw) so data can be entered in the right format.
Analysis & BESS Sizing | Load Data | Sheet | — | Which worksheet holds the load data (for .xlsx uploads).
Analysis & BESS Sizing | Load Data | Header row | row # | The row number that contains the column titles.
Analysis & BESS Sizing | Load Data | Timestamp columns | combined / split | Whether the date and time are in one column (combined) or two separate columns (date + time).
Analysis & BESS Sizing | Load Data | Interval timestamp | End / Start | Whether a reading's timestamp marks the end or the start of its interval. This decides which readings fall inside the 14:00–22:00 sizing window.
Analysis & BESS Sizing | Load Data | Timestamp column | — | Column holding the combined date+time (when timestamp columns = combined).
Analysis & BESS Sizing | Load Data | Date column / Time column | — | Columns holding the date and the time (when timestamp columns = split).
Analysis & BESS Sizing | Load Data | Load column | kW | Column holding the demand/load readings.
Analysis & BESS Sizing | Load Data | PV generation column (optional) | kW | Optional on-site PV generation; used when PV basis uses detected PV (subtracted from load).
Analysis & BESS Sizing | Load Data | Grid export column (optional) | kW | Optional energy exported to the grid (subtracted from load).
Analysis & BESS Sizing | Load Data | Unit | kW / MW / W | Unit of the load readings (converted to kW internally).
Analysis & BESS Sizing | Load Data | Interval (minutes) | min | Time step of the readings (e.g. 30). The tool verifies the readings tile the 14:00–22:00 window.
Analysis & BESS Sizing | Validation summary | Raw readings | # | Total rows found in the uploaded file.
Analysis & BESS Sizing | Validation summary | Parsed readings | # | Rows successfully parsed into timestamp + load.
Analysis & BESS Sizing | Validation summary | Invalid readings | # | Rows that could not be parsed.
Analysis & BESS Sizing | Validation summary | Duplicate readings | # | Repeated timestamps.
Analysis & BESS Sizing | Validation summary | Days | # | Distinct calendar days in the profile.
Analysis & BESS Sizing | Validation summary | Complete days | # | Days with every expected interval inside 14:00–22:00. Only these are used for sizing.
Analysis & BESS Sizing | Validation summary | Incomplete days / missing intervals | # | Days with gaps or off-window readings (excluded from sizing).
Analysis & BESS Sizing | Chart | Chart view | Highest demand / Governing Energy | Which day to plot: the day with the single highest load, or the day that drives the battery size (most energy to shave).
Analysis & BESS Sizing | Chart | Highest demand (KPI) | kW · date | The highest demand reading found in the whole profile (peak demand).
Analysis & BESS Sizing | Chart | Governing energy day (KPI) | kWh · date | The day whose shaving needs the most energy — this day sets the battery size.
Analysis & BESS Sizing | Chart | Load (before PV) [legend] | kW | Customer's demand before any PV offset (grey line).
Analysis & BESS Sizing | Chart | Shave-to target [legend] | kW | Horizontal target line — the level demand is shaved down to (red dashed line).
Analysis & BESS Sizing | Chart | Battery discharge [legend] | kW | Green bars — the power the BESS discharges each interval (load above target, capped by available power and energy).
Analysis & BESS Sizing | Chart | Grid after BESS [legend] | kW | The demand seen by the grid after discharge (load − discharge). If it stays at/below the target, the sizing is sufficient.
Analysis & BESS Sizing | Chart | Peak before | kW | Peak load before the BESS acts.
Analysis & BESS Sizing | Chart | Peak after | kW | Peak grid demand after the BESS acts.
Analysis & BESS Sizing | Chart | Peak reduction | % | (Peak before − Peak after) ÷ Peak before × 100.
Analysis & BESS Sizing | Sizing controls | Sizing strategy | Static / Dynamic / Constant | How the BESS is commanded. Static Threshold: shave every interval above the target. Dynamic Discharge: follow the target across each day. Constant Discharge: apply a fixed kW.
Analysis & BESS Sizing | Sizing controls | Shave-to Target Grid Load | kW | The demand level to shave down to. Lower = shave more of the peak.
Analysis & BESS Sizing | Sizing controls | Auto-calculate sustainable target | — | Finds the lowest target the current pack count can sustain (given reserve margin and power limit).
Analysis & BESS Sizing | Sizing controls | Discharge power (Constant strategy) | kW | Fixed discharge power used when the strategy is Constant Discharge.
Analysis & BESS Sizing | Sizing controls | Reserve margin | % | Safety cushion added to the required energy: energy packs = ceil(required energy × (1 + reserve) ÷ usable per pack). Higher reserve = bigger battery, more headroom. Default 10%.
Analysis & BESS Sizing | Sizing controls | Battery model | — | Which library model (pack) the sizing uses.
Analysis & BESS Sizing | Sizing controls | Design sizing year | 15 | Energy capacity is derated to Year 15 (degradation). Power is NOT degradation-derated.
Analysis & BESS Sizing | Sizing controls | PV basis | No PV / Estimated | Whether the load is net of PV. 'Estimated' subtracts a shaped PV curve derived from the monthly PV energy + peak power (preliminary).
Analysis & BESS Sizing | Sizing controls | Monthly PV energy | kWh | Estimated monthly PV generation (preliminary, not bankable).
Analysis & BESS Sizing | Sizing controls | PV peak power | kW | Estimated PV system peak power (preliminary, not bankable).
Analysis & BESS Sizing | Sizing controls | Sizing window (fixed) | 14:00–22:00 | The peak-tariff window. Only demand inside this window drives the demand charge, so only it is shaved.
Analysis & BESS Sizing | Sizing controls | Operational control window (Start / End) | time | When the BESS is allowed to discharge. Should cover the full 14:00–22:00 sizing window.
Analysis & BESS Sizing | Recommended sizing (results) | Governing day | date | The day with the highest required shaving energy.
Analysis & BESS Sizing | Recommended sizing (results) | Required energy | kWh | Energy the BESS must deliver on the governing day to shave to the target.
Analysis & BESS Sizing | Recommended sizing (results) | Energy packs | # | Number of packs needed for energy (rounded up).
Analysis & BESS Sizing | Recommended sizing (results) | Nameplate (gross) | kWh | Total gross (nameplate) energy = packs × gross kWh per pack.
Analysis & BESS Sizing | Recommended sizing (results) | Usable capacity | kWh | Total usable energy at Year 1.
Analysis & BESS Sizing | Recommended sizing (results) | Year-15 usable capacity | kWh | Total usable energy at Year 15 (degradation-derated).
Analysis & BESS Sizing | Recommended sizing (results) | Required power | kW | Peak instantaneous discharge needed to shave the peak interval.
Analysis & BESS Sizing | Recommended sizing (results) | PCS quantity | # | Number of PCS (inverters) needed to deliver the required power.
Analysis & BESS Sizing | Recommended sizing (results) | Power-constrained packs | # | Packs needed for power. If this exceeds energy packs, the battery is power-limited (a warning is shown).
Battery & PCS Library | Model fields (form + Excel) | Model_ID | text | Unique stable identifier (not shown in the UI; used by the Excel import — duplicate IDs are rejected).
Battery & PCS Library | Model fields (form + Excel) | Brand | text | Manufacturer or supplier name.
Battery & PCS Library | Model fields (form + Excel) | Name / Model_Name | text | Customer-facing battery model name.
Battery & PCS Library | Model fields (form + Excel) | Gross Pack kWh | kWh | Nameplate energy of one battery pack/container.
Battery & PCS Library | Model fields (form + Excel) | Min SOC % | % | Minimum allowed state of charge (operating floor).
Battery & PCS Library | Model fields (form + Excel) | Max SOC % | % | Maximum allowed state of charge (operating ceiling).
Battery & PCS Library | Model fields (form + Excel) | RTE % | % | Round-trip efficiency (AC-to-AC system RTE).
Battery & PCS Library | Model fields (form + Excel) | Auxiliary factor % | % | Auxiliary retention factor (98% means a 2% auxiliary loss).
Battery & PCS Library | Model fields (form + Excel) | Pack rated power kW | kW | Maximum discharge power of one pack.
Battery & PCS Library | Model fields (form + Excel) | PCS rated power kW | kW | Rated AC power of one PCS/inverter.
Battery & PCS Library | Model fields (form + Excel) | First-year degradation % | % | Capacity loss in year 1.
Battery & PCS Library | Model fields (form + Excel) | Annual degradation (years 2–15) % | % | Capacity loss per year in years 2–15.
Battery & PCS Library | Model fields (form + Excel) | RTE definition | text | Free-text description of the RTE basis.
Battery & PCS Library | Model fields (form + Excel) | Degradation / reserve notes | text | Notes on degradation / reserve assumptions.
Battery & PCS Library | Model fields (form + Excel) | Source notes | text | Where the values came from (datasheet vs illustrative example).
Battery & PCS Library | Derived (calculated) | DoD % | % | Depth of discharge = Max SOC % − Min SOC % (calculated).
Battery & PCS Library | Derived (calculated) | Year-15 SOH % | % | State of health at Year 15 = (1 − first-year deg %) × (1 − annual deg %)^14 × 100.
Battery & PCS Library | Derived (calculated) | Usable per pack (birth) | kWh | Usable energy per pack with no degradation = gross kWh × DoD % × RTE % × aux %.
Battery & PCS Library | Derived (calculated) | Usable per pack (Year 1) | kWh | Birth usable × (1 − first-year deg %).
Battery & PCS Library | Derived (calculated) | Usable per pack (Year 15) | kWh | Birth usable × Year-15 SOH %. Shown in the library table as 'Usable Y15'.